## Slide 1
Water Quality Mixing Model for EFN: 2 Case Studies
Gabe Sentlinger (Fathom Scientific Ltd)
©Fathom Scientific 2020
Culliton CreekHydropower Project (Squamish, B.C. )
Boulder Creek Hydropower Project
(Pemberton, B.C.)
Mixing Reach ~430m
Width ~10-20m
Mixing Reach ~190m
Width ~10-15m

## Slide 2
Culliton Creek near Squamish B.C.
Boulder Creek near Pemberton B.C.
Both:
-have a run-of-river hydropower project on their lower reaches.
-Tailrace Q uncertainty generally +/-1%
-are very active waterways with hydraulic control that changes often.
-have Environmental Flow Needs (EFNs) in the water license that require a Grade A (<7% Uncertainty) or Grade B (<15% Uncertainty).
-are time consuming (expensive) to get to.
-difficult to measure in conventional ways.

## Slide 3: Constant Rate Tracer Method
Where DS is Downstream,
US is Upstream
R is Reference
W is Conservative Water Quality such as Temperature or Temperature Compensated Electrical Conductivity (ECT)

## Slide 4: Constant Rate Tracer Method for Hydropower
-We can apply this same concept to a confluence of streams, where one input Q, QR, is known to a high accuracy AND inputs a significantly detectable amount of tracer.
-This is the case for a Hydropower project.
=

## Slide 5: Culliton Creek Probe Locations: Looking Upstream
US PH Gauge
Tailrace Gauge
-In 2016-2017 we installed high accuracy-high resolution ECT and Temp gauges Upstream of the Powerhouse, in the Tailrace, and Downstream of the Powerhouse at Culliton Creek as a Proof of Concept experiment.

## Slide 6: Culliton Creek Probe Locations: Looking Downstream
DS PH ECT Gauge
Small ditch inflow
-DSPH gauge is downstream of mixing length and upstream of local inflow.
-It was very tricky to position the gauges to sample moving, non- aerated water free from any local influences.
-Avoid backeddies, subsurface inflow, pools, turbulence.
-Keep the mixing reach as short as possible.
-We also had the benefit of an active water level gauge with an active rating curve.
Existing Active Water Level Gauge with Rating Curve

## Slide 7
Culliton Creek DSPH gauge temperatures and EC.T values in between the USPH and the Tailrace (Reference)
US PH Gauge experiences freezing temperatures
Freezing affects EC.T
Storm causes dWQ = 0
U1 shut off
Top figure compares the Tailrace Q to the Active DS PH Gauge.

## Slide 8
Culliton Creek DSPH gauge temperatures and EC.T values in between the USPH and the Tailrace (Reference)
Air Temp >Water temp so USPH flips
Fouling by sediment, air entrainment cause all kinds of trouble for Tailrace EC

## Slide 9
-ThreshDS_T_Q is the Temperature Derived Q after a Delta T Threshold is applied.
-ECMM works in theory, but difficult to maintain required accuracy.
-TMM works very well with little maintenance.
-Using a min dT of 0.17oC and min dEC.T of 1uS/cm. U1Q > 0 and US T > 0.2 oC.
Results
Peak event of 19 cms

## Slide 10
-Blue is established RC.
-Evidence to support adjusting lower end of RC.
Manual measurements agree better with TMM
Existing RC probably overestimating low flows
Results: Compared to Established RC

## Slide 11
Results: Compared to RC
-RC retrained using manual measurements and TMM results.
- A histogram of dT vs %Error between new RC and TMM derived Q
-Error explodes below 0.2°C. 95% confidence for 7% error at 1.0°C.
-If the error is random, averaging n measurements could reduce error by 1/sqrt(n).

## Slide 12: Culliton Creek Summary
-WQMM potentially powerful method to estimate Q continuously from known Q (PowerPlant) and Temp and/or EC.
-Currently best to use in conjunction with stage record to assist in RC derivation.
-Currently active as realtime report

## Slide 13
Boulder Creek: Compared to RC
-Not as much data at Boulder (installed Sep 3, 2019: last data Oct 27, 2019)
-Longer Mixing (430m vs 130m) meant more solar influx during summer (heating up to 0.1°C
-Needed to relocate Tailrace probe to avoid backeddy and subsurface inflow
-More remote location resulted in fewer visits
-Required accuracy of temperature probes: 0.04°C.
-Minimum DT 0.23°C. Minimum Tailrace Q 0.5cms.

## Slide 14
-Have not yet compensated for thermal flux.
-Largest components are likely Solar Radiation and Evaporation
(From Boyd and Kasper 2003: Heat Source Model V0.7)
Possible solution: Only consider inflection points (7am-8am)

## Slide 15
Boulder Creek: Compared to RC
-Only 2 validation points for this site and period. Validation agreed with TMM (within uncertainty), however RC Q was not accurate.
-Current State: Trying to tie everything into Plant HMI-PLC to have alternate method of EFN Q.
Initial Temp Probe Placement in backeddy at lower Tailrace Q and also subject to subsurface inflow
Moved it slightly DS

## Slide 16
Boulder Creek: Summary
-Longer mixing reach resulted in warming of 0.1°C in September, beyond required accuracy of 0.04 °C. Results were best when air temp and stream temp closer (October).
-Many pitfalls in probe placement (subsurface flow, drying, freezing, backeddy)
-In theory, once probe placement sorted and temp probes calibrated to within 0.04°C, continuous Q based on dT and Tailrace Q.
-Build heat flux model to further reduce error.
DS EC-T Probe Placement (no issues)

## Slide 17
-If you assume the heating of the water column is just error, , then it’s a linear component of the error function
WQMM Uncertainty
-Error of 1-5% based on daily averages, larger for instantaneous. But we also get a larger dT signal, so it’s a negative feedback loop (self-regulating).
The larger the Q, the lower the Ii error
The lower the Swept Area, the lower the Ii error

## Slide 18
WQMM: Summary
-Possible to use the Powerhouse as a very expensive flow meter.
-Requires high accuracy temp probes (~0.04 °C)
-Requires calibration of probes. Trying to achieve 0.02oC Accuracy.
-More studies required.
Thank you BluEarth Renewables and Innergex Renewable Energy Corp.