## Slide 1: Towards energy autonomy of small Mediterranean islands: Challenges, perspectives and solutions
Athanasios Zisos, Maria-Eleni Pantazi, Marianna Diamanta, Ifigeneia Koutsouradi, Anna Kontaxopoulou, Ioannis Tsoukalas, Georgia-Konstantina Sakki, and Andreas Efstratiadis Department of Water Resources & Environmental Engineering National Technical University of Athens, Greece
European Geosciences Union General Assembly, Vienna, Austria & Online | 23–27 May 2022
HS5.2 – Innovation in Hydropower Operations and Planning to Integrate Renewable Energy Sources and Optimize the Water-Energy Nexus

## Slide 2: Motivation: Ensuring energy autonomy for Sifnos island
General characteristics:
Located in the western Cyclades complex
Area: 74 km2
Permanent population: 3 203 inhabitants
Up to 100 000 tourists during summer
Major geological formation: Dolomitic marble
Source: Google Earth
Source: Wikipedia
Profile of current energy supply system:
Non-interconnected island
Energy production from a 9.0 MW oil power station
Small share from renewables (1.2 MW wind, 0.2 MW PV)
Total annual energy demand (2021): 17.3 GWh
Peak energy demand (summer period): 5.4 MW
Projected peak demand: 8.0 MW
Research objective: Design of a hybrid power system based on seawater pumped-storage and two renewables (solar, wind)
Further info: Katsaprakakis & Voumvoulakis (2018)

## Slide 3: Conceptual scheme of proposed hybrid power system
Wind turbines Enercon E70 & E44
Photovoltaic park
Number of panels: NP
Nominal power: 340 kW
Panel area: 1.94 m2
Wind velocity
Solar radiation
Wind power
Solar power
Power demand
Power surplus/ deficit
Actual storage S
Power accounting
Reservoir
Penstock
Power station
Turbine/pump
Sea
Generator
Storage capacity: Smax
Total head: 320 m
Hydraulic losses: 15 m
Efficiency: 80-85%
Setup of design optimization: Estimation of reservoir capacity and PV park size (number of panels) in order to maximize the anticipated net profit and system’s reliability
Rainfall
Evaporation

## Slide 4
Stochastic simulation-optimization approach
System driven by inherently uncertain processes, i.e., meteorological and socioeconomic.
Stochastic simulation-optimization approach (Sakki et al., 2022), by using the anySim model (Tsoukalas et al., 2020) to provide synthetically generated hourly data for:
  Wind velocity
  Power demand (socioeconomic process)
Application of a typical annual profile for other meteo-rological processes (solar radiation, rainfall, evaporation).
System design optimization under multiple input data scenarios of 10 years length.
Preliminary investigations impose the use of a suitable turbine mix to maximize the available wind potential (key challenge: avoid energy losses due to often cut-offs).

## Slide 5
Outcomes of simulation procedure
System outputs:
Energy fluxes (power generation per source, power consumption due to pumping)
Water fluxes (reservoir storage, penstock flow)
Financial fluxes (depreciated construction costs, maintenance costs, energy production revenues)
Reservoir storage (m3)
Sharing of energy production (MWh)
January
June

## Slide 6
Optimization under uncertainty
Investigation of two optimization settings:
  Setting A: Minimization of system’s failure probability (= frequency of power deficits)
  Setting B: Full depreciation of investment costs for given time horizon
The two settings provide substantially different results, yet setting B ensures a more economic design (impressive reduction of reservoir size, reduction of PV panels), with minimal decrease of reliability.
 | Setting A | Setting B
Number of solar panels | 3 587 (562) | 2 825 (1 085)
Reservoir capacity | 443 340 (170 019) | 89 313 (17 914)
Reliability (%) | 82.81 (1.22) | 78.58 (1.51)
Investment costs (106 €) | 30.60 | 19.60
Summary results of the two stochastic optimization settings (mean values of synthetic scenarios, standard deviations in parentheses)
Multiple combinations of optimized design variables, induced by wind and power demand uncertainty.

## Slide 7
Source: Yoon and Oh (2015)
Source: Plastika Kritis S.A.
Other engineering challenges & provided solutions
Pipe erosion:
Pipe material: GRP
Significant reduction of friction losses
Increased durability to UV radiation
Achieving flow velocity within safety limits (0.6 – 6.0 m/s)
Tank waterproofing:
Application of HDPE geomembranes
High resistance in tension, puncture, environmental stress cracking and chemicals
Erosion of electro-mechanical equipment:
Stainless steel equipment
High resistance in seawater erosion

## Slide 8
References
Katsaprakakis, D. A., and M. Voumvoulakis, A hybrid power plant towards 100% energy autonomy for the island of Sifnos, Greece. Perspectives created from energy cooperatives, Energy, 161, 680-698, doi:10.1016/j.energy.2018.07.198, 2018.
Sakki, G.-K., I. Tsoukalas, P. Kossieris, I. C. Makropoulos, and A. Efstratiadis, Stochastic simulation-optimisation framework for the design and assessment of renewable energy systems under uncertainty, Renewable and Sustainable Energy Reviews, 2022 (submitted; preprint available at https://ssrn.com/abstract=4109850).
Tsoukalas, I., P. Kossieris, and C. Makropoulos, Simulation of non-Gaussian correlated random variables, stochastic processes and random fields: Introducing the anySim R-Package for environmental applications and beyond, Water, 12(6), 1645, doi:10.3390/w12061645, 2020.
Yoon, S. H., and J. O. Oh, Prediction of long term performance for GRP pipes under sustained internal pressure, Composite Structures, 185-189, 134, doi:10.1016/j.compstruct.2015.08.075, 2015.
Zisos et al., Towards energy autonomy of small Mediterranean islands: Challenges, perspectives and solutions